|  | WHAT? A properly sealed heating and cooling duct system can: - Reduce utility bills by up to 20% - Increase comfort throughout the home - Improve IAQ by reducing moisture, dust, and pollen |
| --- | --- |
|  | WHY? As conditioned air escapes ducts supplying heating and cooling, occupants need to run systems longer to create a comfortable living space. Poorly sealed return ducts in unconditioned spaces can potentially draw in contaminated air and spread contaminants throughout the house. |
|  | HOW? - All duct leaks, connections, and plenums shall be sealed with UL-approved mastic, UL 181 tape, or equivalent. - For additional strength with seams that are wider than 1/8 inch, cover the gap with fiberglass mesh tape, then apply the mastic. - Regular cloth-backed duct tape should not be used because it can dry out and fail quickly. |

MORE ABOUT TIGHT DUCT SEALING